ANNEXURE : A

Detail List of Materials and Specific Terms & Conditions

Name of Work: 	Supply, Installation, Configuration and Commissioning of RFID cum Biometric (Finger-print) based E/M lock backed with CCTV system at Jaduguda and Turamdih units of UCIL.

Prequalification Criteria:

- Bidder shall be registered vendor of the supplied make of Access control system

- Bidder shall have executed the access control system (consisting of Biometric reader and E/M lock) in an organization of repute.

Scope of work	: 	Supply, Installation, Configuration and Commissioning of RFID cum Biometric (Finger-print) based E/M lock. Real time recording of with the help of CCTV camera and Digital Video recorder (DVR) for the operation of system at server rooms and control rooms of Jaduguda and Turamdih units of UCIL.

Proposed Area of Installation:

JADUGUDA UNIT

- EDP Section of Account

- Ion-Exchange Control Room

- Drying Unit Control Room

TURAMDIH UNIT

- Central Control Room

- Fine Crushing Control Room

- Primary Crushing Control Room

- ETP Control Room

Exclusion	:	Any modification in the existing gate is in not in the scope of this job. Bidder may inspect the existing gate and suggest modification (if required) including submission of modification sketches/drawing for installation of E/M locks & Card cum Biometric reader within 30 days of placement of order. Modification of gate if required shall be done by the purchaser.

Functional requirement: The RFID cum Biometric E/M lock is planned to be installed at the entry point of Server cum Control room. Each employee has already been provided with Mifare RFID identity cards. Database (Card & Biometric data) of the permitted employee shall be initially stored in the Card cum Biometric Readers. All Reader shall work independently. The Operation of all gate shall be backed by a CCTV Camera with recorder.

Card reader shall function in Card Mode Only/Biometric Mode only or Card Cum Biometric mode. Administrator shall select the desired mode during configuration of the system.

Entry procedure: Initially door will be locked with the supplied E/M lock. For accessing the entry employee shall flash his RFID Card and/or put his registered finger on the scanner of supplied reader. Machine will compare the data received and compare from its database and if the employee data matches with the data stored in the permission category list, Reader will command the E/M lock to operate for the predefined time say 5 seconds. During this time Employee shall enter the Server/Control room.

Exit Procedure: Employee shall press the exit button (installed inside the room) E/M lock shall open and employee exit the room.

Completion Time: The entire work shall be completed within 4 months from the placement of order

Delivery: The Delivery of the supply shall be done at UCIL Turamdih Stores. Purchaser in consultation with the supplier shall make arrangement to transportation of the required  goods to Jaduguda.

Warranty: all supplied item shall be warranted for trouble free operation for One year from date of commissioning

Security deposit: 5% of the ordered value shall be deposited as security deposit within 15 days of placement of order.

Payment Terms:

a. Supply Part: 80% of supply part shall be paid within 30 days after supply and acceptance of goods at central stores.

b. Service part: Balance 20% of supply part along with 100% of service charges within 30 days after successful commissioning and handing over of system.

Power supply: All the Items/Material shall work on 230V AC power supply, Incase the supplied item suits any other supply, and suitable power adopter shall be supply free of cost. One 230V AC supply shall be provided within 5 meters of installation at each site, further distribution is in the scope of bidder

Technical Specification

RFID (Mifare) card cum Biometric (Fingerprint) reader

| RFID (Mifare Card Cum Biometric (fingerprint reader) |  |  |  |  |
| --- | --- | --- | --- | --- |
| 1 | Storage capacity | Fingerprints templates | 10000 |  |
|  |  | Card Storage | 10000 |  |
|  |  | Transaction storage | 1,00,000 |  |
| 2 | Card Reader Type | Card reader | Inbuilt: RFID Mifare Card reader |  |
|  |  |  | (optional: proximity card reader/ HID prox) |  |
| 3 | Central Processing Unit |  | 800 Mhz 32 bit Microprocessor |  |
| 4 | Biometric | Fingerprint sensor | 500 DPI Optical sensor |  |
|  |  | Identification speed | <0.5 sec |  |
| 5 | False Acceptance Rate | FAR | <=0.0001% |  |
| 6 | False Rejection Rate | FRR | <=1% |  |
| 7 | Audio/ Visual/ keypad | Display | 3" Color TFT |  |
|  |  | Keypad | Yes |  |
|  |  | LED Indicator | Green/Red |  |
|  |  | Schedule Bell/Speaker | Mini Speaker |  |
| 8 | Communication | Communication | TCP/IP, USB, ( Optional : Wifi, GPRS) |  |
|  |  | Push data | yes (support both static IP and domain server) |  |
|  |  | Standard features | work code,SMS,DLST, Self service query, Status Switch |  |
| 9 | Power & environment | Power Supply | 230V AC ±10%, 50Hz |  |
|  |  | Operating Temperature | 5 Deg. C to 45 Deg. C |  |
|  |  | Operating Humidity | 20% to 80% |  |
| 10 | Access control | Wiegand | In & Out both 26 or 34 bit (With or without site code) |  |
|  |  | Relay | 12 V relay for lock EM lock, Bolt Lock or Strike lock |  |
|  |  | Door Sensor | Yes |  |
|  |  | Anti Pass back | Yes |  |
|  |  | Door Bell | Yes |  |
| 11 | Exit Readers | Support exit readers | Yes |  |
| 12 | Compatibility |  | Compatible with Multi Door controllers via weigand |  |
| 13 | Software to be supplied along the reader |  | Desktop application for data fetching from Reader, report customization and report generation. |  |
| 14 | Compatible Software and SDK |  | Supports 3rd Party Payroll/ HRMS/ERP and Other applications |  |
|  |  |  | SDK for desktop applications |  |
| E/M Lock |  |  |  |  |
| 1 | Power |  | 12V |  |
| 2 | Current rating |  | Vendor to Specify |  |
| 3 | Holding Force |  | 600lbs |  |
| 4 | Holding Capacity |  | 230Kg |  |
| 5 | Temperature |  | 0°C – 55°C |  |
| 6 | Operating Humidity |  | 0%-95% (Non-Condensing) |  |
| 7 | Anti-Rust Surface Treatment |  | Zinc Plating |  |
| 8 | Suitable for |  | Wooden door, Glass door, Alluminium door, Fireproof door |  |
| 9 | Optional Accessories |  | to be supplied with suitable bracket |  |
| 10 | Status LED |  | Green/red indication for lock status |  |
| 11 | Protection |  | Voltage and current spike protection PCB |  |
| 12 | Feature |  | Request-to-open, Auto-relock if no Action |  |
| 13 | Silent operation |  | no humming or buzzing |  |
| CCTV Camera (Analog output) |  |  |  |  |
| 1 | Image Sensor: | : | 2MP CMOS Image Sensor |  |
| 2 | Signal System: | : | PAL/NTSC |  |
| 3 | Effective Pixels: | : | 1920(H)*1080(V) |  |
| 4 | Shutter Time: | : | 1/25(1/30) s to 1/50,000 s |  |
| 5 | Day& Night: | : | Color |  |
| 6 | Video Frame Rate: | : | 1080p@25fps/1080p@30fps |  |
| 7 | HD Video Output: | : | 1 Analog HD output |  |
| 8 | Synchronization: | : | Internal Synchronization |  |
| 9 | Menu |  |  |  |
| 10 | White Balance: | : | Auto/MWB |  |
| 11 | BLC: | : | Support |  |
| 12 | AGC: | : | Support |  |
| 13 | General |  |  |  |
| 14 | White Light: | : | Up to 30 m |  |
| 15 | Operating Conditions: | : | Temp.: 5 °C - 50 °C |  |
|  |  | : | Humidity 90% or less (non-condensing) |  |
| 16 | Power Supply: | : | 230V AC |  |
| 17 | Weather Proof: | : | IP67 |  |
| CCTV Camera (IP Based) |  |  |  |  |
| 1 | Camera |  |  |  |
| 2 | Image Sensor: | : | 1/2.8" Progressive Scan CMOS |  |
| 3 | Signal System: | : | PAL/NTSC |  |
| 4 | Min. Illumination: | : | Color: 0.005 Lux (AGC ON), 0 Lux with IR |  |
| 5 | Shutter time: | : | 1/3 s to 1/100,000 s |  |
| 6 | Lens: | : | 2.8 mm, horizontal field of view: 108° |  |
| 7 | Day& Night: | : | IR cut filter with auto switch |  |
| 8 | Wide Dynamic Range: | : | 120 dB |  |
| 9 | Digital noise reduction: | : | 3D DNR |  |
| 10 | Focus: | : | Fixed |  |
| 11 | Compression Standard |  |  |  |
| 12 | Video Compression: | : | H.265+/H.265/H.264+/H.264/MJPEG |  |
| 13 | Video bit rate: | : | 32Kbps~16Mbps |  |
| 14 | No. of streams Streams: | : | 2 |  |
| 15 | Image |  |  |  |
| 16 | Max. Image Resolution: | : | 1920 x 1080 |  |
| 17 | Frame Rate: | : | 50Hz: 50fps (1920 × 1080, 1280 × 960, 1280 × 720) |  |
| 18 | Sub Stream: | : | 50Hz: 25fps (640 × 480, 640 × 360, 352 × 288) |  |
| 19 | Image Enhancement: | : | BLC/ DNR/ROI/HLC |  |
| 20 | Image Settings: | : | Rotate mode, saturation, brightness, contrast, sharpness and white balance adjustable by client software or web browser |  |
| 21 | Day/Night Switch: | : | Day/Night/Auto/Schedule |  |
| 22 | Network |  |  |  |
| 23 | Alarm Trigger: | : | Motion detection, network disconnected, IP address conflict, illegal login, HDD full, HDD error |  |
| 24 | Protocols: | : | TCP/IP, UDP, ICMP, HTTP, HTTPS, FTP, DHCP, DNS, DDNS, RTP, RTSP, RTCP, PPPoE, NTP, UPnP, SMTP,, 802.1X, QoS, IPv6 |  |
| 25 | General Function: | : | One-key reset, Anti-Flicker, heartbeat, mirror, password protection, privacy mask, Watermark, IP address filtering |  |
| 26 | System Compatibility: | : | ONVIF (Profile S, Profile G) |  |
| 27 | Communication Interface: | : | 1 RJ45 10M / 100M Ethernet interface |  |
| 28 | On-board storage: | : | Built-in Micro SD/SDHC/SDXC slot |  |
| 29 | Smart Features | : | Line crossing detection, Intrusion detection, Unattended baggage detection, Object removal detection & Scene change detection |  |
| 30 | Operating Conditions: | : | Temperature : 5 °C ~ 45 °C |  |
|  |  | : | Humidity 95% or less (non-condensing) |  |
| 31 | Power Supply: | : | 12 VDC ± 25%, PoE (802.3af Class3) |  |
| 32 | Power Consumption: | : | 12 VDC ± 25%, 5W |  |
|  |  | : | PoE(802.3af, class 3), 6.5W |  |
| 33 | Weather Proof: | : | IP67 |  |
| 34 | IR Range: | : | Up to 30m |  |
| Power Supply |  |  |  |  |
| 1 | Input voltage | : | 180 to 264VAC |  |
| 2 | Output voltage | : | 12V DC |  |
| 3 | Output Current Range | : | 0 to 10A |  |
| 4 | Ripple & Noise | : | 100mVp-p (Max) |  |
| 5 | Rated Power | : | 120W |  |
| 6 | Voltage Adj. Range | : | 11.4 to 13.2V |  |
| 7 | Voltage Tolerance | : | less than ±2.0% |  |
| 8 | Line Regulation | : | less than ±1.0% |  |
| Digital Video Recorder |  |  |  |  |
|  | Features | : | Description |  |
| 1 | Type of DVR | : | Shall be on Embedded operation system |  |
| 2 | Operation mode | : | Previews ,Records ,Playback ,Back Up, Network |  |
| 3 | Number of Video input | : | 4/8 Channels of 960P/720P or D1 Res. |  |
| 4 | Compression Method | : | Must be in H.264 / MPEG-4 |  |
| 5 | Recording Resolution | : | Programmable among 1080P@30fps, 720@30fps, VGA, 4CIF, 2CIF, CIF & QCIF and other supported resolution |  |
| 6 | Recording Mode | : | Boot ,Timing ,Motion Detection |  |
| 7 | Password security | : | 2 Levels , Admin+ Users |  |
| 8 | Video Motion Detection & Recording Configuration | : | Independent Channel configuration |  |
| 9 | Video Out | : | 1 VGA and 1 HDMI |  |
| 10 | HDMI Resolution | : | 1-ch, resolution: 1920*1080P/60Hz, 1600*1200/60Hz, 1280*1024/60Hz, 1280*720/60Hz, 1024*768/60Hz, 1-ch, resolution: 1920*1080P/60Hz, 1920*1080P/50Hz, |  |
| 11 | VGA Resolution | : | 1600*1200/60Hz, 1280*1024/60Hz, 1280*720/60Hz, 1024*768/60Hz |  |
| 12 | Display windows: | : | 1 / 4 / (Single / Quad window mode) |  |
| 13 | Play backup | : | Support Simultaneously 4 channel |  |
| 14 | Min. Internal HDD supported (TB) | : | 1 internal hard disks (storage capacity: 6TB each) |  |
| 15 | Internal HDD Interface | : | SATA HDD interface |  |
| 16 | Backup | : | Automatic Scheduled backup |  |
| 17 | Backup Storage Media | : | Backup through USB or network |  |
| 18 | Network Port | : | 1no. of self-adaptive RJ45 Port 10M/100M/1000M |  |
| 19 | Backup Interface | : | Internal/External shall provided |  |
| 20 | Scheduled Backup | : | Programmable |  |
| 21 | PTZ Connectivity | : | Supports multi PTZ protocols |  |
| 22 | Remote Access Software | : | To be supplied along with equipment |  |
| 23 | Web Browsing | : | IE, google-Crome, Mozilla browsers supported |  |
| 24 | Operating Voltage | : | 230V AC |  |
| Network Video Recorder |  |  |  |  |
| 1 | Video/Audio Input |  |  |  |
| 2 | IP video input: | : | 8-ch |  |
| 3 | Two-way audio input: | : | 1-ch, RCA (2.0 Vp-p, 1kΩ) |  |
| 4 | Network |  |  |  |
| 5 | Outgoing bandwidth: | : | 80Mbps |  |
| 6 | Incoming bandwidth: | : | 80Mbps |  |
| 7 | Video/Audio Output |  |  |  |
| 8 | HDMI Output: | : | 1-ch, resolution: 1920*1080P/60Hz, 1600*1200/60Hz, 1280*1024/60Hz, 1280*720/60Hz, 1024*768/60Hz |  |
| 9 | Recording Resolution: | : | 4MP/3MP/1080p/UXGA/720p/VGA/4CIF/DCIF/2CIF/CIF/QCIF |  |
| 10 | Audio Output: | : | 1-ch, RCA (Linear, 1kΩ) |  |
| 11 | VGA Output: | : | 1-ch, resolution: 1920*1080P/60Hz, 1280*1024/60Hz, 1280*720/60Hz, 1024*768/60Hz |  |
| 12 | Decoding |  |  |  |
| 13 | Capability: | : | 1-ch @ 8 MP / 4-ch @ 1080p |  |
| 14 | Live view / Playback: | : | 8 MP/6 MP/5 MP/4 MP/3 MP/1080p/UXGA /720p/VGA/4CIF/DCIF/ 2CIF/CIF/QCIF |  |
| 15 | Hard Disk |  |  |  |
| 16 | SATA: | : | 1 SATA interface for 1 HDD |  |
| 17 | Capacity: | : | Up to 6TB capacity for each HDD |  |
| 18 | External Interface |  |  |  |
| 19 | Network Interface: | : | 1RJ-45 10/100/1000Mbps self-adaptive Ethernet interface |  |
| 20 | USB Interface: | : | 2, USB2.0 |  |
| 21 | General |  |  |  |
| 22 | Power Supply: | : | 230V AC |  |
| 23 | Working Temperature: | : | 5 Deg. C to 50 Deg. C |  |
| 24 | Working Humidity: | : | 10 % ~ 90 % |  |
| Media Converter |  |  |  |
| 1 | Standards | : | IEEE802.3u100BASE-TX, l00BASE- FX (Fast Ethernet,100Mbps) |  |
|  |  | : | Supports Full Duplex Ethernet Mode. |  |
| 2 | Fiber Optic Connectors | : | Two connectors are provided for fiber optic cable connection. One is labeled "Tx" for Transmission of optical data; the other is labeled "Rx" for reception of optical data. |  |
| 3 | Ethernet Connectors | : | Standard RJ-45 port is provided for connecting to Ethernet. |  |
| 4 | LED Interface | : | Two LED’s are provided one for detecting the Fiber Link and the other for detecting the Tx(Ethernet) Link. |  |
|  |  | : | When units are connected and there is data transfer both the LED’s are blinking simultaneously. |  |
| 5 | Adaptability | : | Wavelength 1310 nm |  |
|  |  | : | Fiber distance : Single mode 15Km |  |
|  |  | : | Fiber : 9/125um Single mode Fiber |  |
| PoE Network switch |  |  |  |  |
| 1 | Ports | : | 8 x 10/100BASE-TX MDI/MDIX Ports |  |
| 2 | PoE Inject Port | : | 8-port with 802.3at/af PoE injector function with Port-1 to Port-8 |  |
| 3 | LED Display | : | LAN/PoE ON: Orange |  |
| 4 | Switch Fabric | : | 2Gbps/non-blocking |  |
| 5 | Switch Throughput@ 64 bytes | : | 1.48Mpps@64 bytes |  |
| 6 | Maximum Frame Size | : | 1522 bytes |  |
| 7 | Flow Control | : | IEEE 802.3x pause frame for full-duplex |  |
| 8 | DIP Switch | : | Selectable operation mode |  |
| 9 | Enclosure | : | Metal |  |
| 10 | Power Requirements | : | AC 100~240V, 50/60Hz, |  |
| 11 | Power Consumption | : | System On: Max. 2.4 watts/8.1 BTU |  |
| 12 | Dissipation | : | Ethernet Full Loading: Max. 5 watts |  |
|  |  |  | PoE Full Loading: Max. 150 watts |  |
| 13 | ESD Protection | : | Contact discharge of 3kV DC |  |
|  |  |  | Air discharge of 3kV DC |  |
| 14 | Thermal Fan | : | Fanless |  |
| 15 | PoE Standard | : | IEEE 802.3af Power over Ethernet/PSE |  |
|  |  |  | IEEE 802.3at Power over Ethernet Plus/PSE |  |
| 16 | PoE Power Supply Type | : | End-span |  |
| 17 | Power Pin Assignment |  | 1/2(+), 3/6(-) |  |
| 18 | PoE Power Output |  | Per port 55V DC, 540mA. max. 30 watts |  |
| 19 | PoE Power Budget |  | 150 watts |  |
| 20 | Number of PDs, 7 watts |  | 8 |  |
| 21 | Number of PDs, 15.4 watts |  | 8 |  |
| 22 | Number of PDs, 30 watts |  | 5 |  |
| 23 | Standard Conformance |  |  |  |
| 24 | EMI Safety |  | CE/LVD EN60950, RoHS |  |
| 25 | Warranty |  | 1 Year |  |
| 26 | Standard Compliance |  | IEEE 802.3 Ethernet |  |
|  |  |  | IEEE 802.3u Fast Ethernet |  |
|  |  |  | IEEE 802.3ab Gigabit Ethernet |  |
|  |  |  | IEEE 802.3x Flow Control |  |
|  |  |  | IEEE 802.3af Power over Ethernet |  |
|  |  |  | IEEE 802.3at Power over Ethernet Plus |  |
| 27 | Operating/Storage Environment Temperature | : | -10 ~ 50°C |  |
| 28 | Operating/Storage Relative Humidity | : | 10~ 95% (non-condensing) |  |
| RFID card |  |  |  |
| 1 | Type | : | Contact-less Smart Card 4KB Blank/White Mifare |  |
| 2 | Dimension | : | 83mm : Width |  |
|  |  | : | 51 mm : length |  |
| 3 | Sensing range | : | upto 50mm |  |
| 4 | Operating Frequency | : | 13.56MHz |  |
| 5 | Feature | : | Unique Card Serial No. |  |

Location wise Requirement of Material

| Sl. No. | Description of Site | No. of Doors | No. of readers with battery, EmLock and exit button | RFID Mifare Card | CCTV Camera |  | Video Recorder with HDD & Monitor |  | PoE Network Switch | Media Conveter (10/100X) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  | Analog Camera | Network Camera | DVR | NVR |  |  |
| Jaduguda Site |  |  |  |  |  |  |  |  |  |  |
| 1 | EDP Section of Jaduguda | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 0 | 0 |
| 2 | Ion Exchange control room | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 0 | 0 |
| 3 | Drying Unit control room | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 0 | 0 |
| 4 | Spare | 0 | 1 | 50 | 1 | 0 | 1 | 0 | 0 | 0 |
| Sub Total of Jaduguda Site |  | 3 | 4 | 50 | 4 | 0 | 4 | 0 | 0 | 0 |
| Turamdih Site |  |  |  |  |  |  |  |  |  |  |
| 5 | CCR at Chemical House | 2 | 2 | 0 | 0 | 2 | 0 | 1 | 1 | 2 |
| 6 | ETP Control Room | 1 | 1 | 0 | 0 | 1 | 0 |  | 1 | 1 |
| 7 | Fine Crushing & grinding Mill control room | 2 | 2 | 0 | 0 | 2 | 0 | 1 | 1 | 2 |
| 8 | Primary crushing Control room | 1 | 1 | 0 | 0 | 1 | 0 |  | 1 | 1 |
| 9 | Spare | 0 | 2 | 50 | 0 | 2 | 0 | 1 | 1 | 1 |
| Sub Total of Turamdih Site |  | 6 | 8 | 50 | 0 | 8 | 0 | 3 | 5 | 7 |
| Total |  | 9 | 12 | 100 | 4 | 8 | 4 | 3 | 5 | 7 |

Bill of Material

|  | Sl. No. | Description of items | Unit | Quantity Required |
| --- | --- | --- | --- | --- |
| Access Control | 1 | Biometric Cum RFID Card reader | No. | 12 |
|  | 2 | Battery for Biometric cum RFID reader | No. | 12 |
|  | 3 | EM LOCKS | No. | 12 |
|  | 4 | EXIT BUTTON | No. | 12 |
|  | 5 | Misc. Hardware | lot | 1 |
| Surveillance System | 6 | CCTV Camera (IP/Network) | No. | 8 |
|  | 7 | CCTV Camera (Analog) | No. | 4 |
|  | 8 | Power Supply for CCTV Camera | No. | 7 |
|  | 9 | 3+1 cable for Analog camera | Meter | 180 |
|  | 10 | DVR (4 - Channel) | No. | 4 |
|  | 11 | 1TB HDD for DVR/NVR | No. | 7 |
|  | 12 | 18.5" CCTV monitor | No. | 7 |
|  | 13 | UTP cable for IP Camera | Meter | 305 |
|  | 14 | NVR (8-Channel) | No. | 3 |
|  | 15 | Media Converter 10/100X | No. | 7 |
|  | 16 | PoE Network Switch | No. | 5 |
|  | 17 | Spare Mifare RFID Card | No. | 100 |
|  | 18 | Misc. Hardware | lot | 1 |

Bill of Services

| Sl. No. | Category | Description of Item | Unit | Quantity |
| --- | --- | --- | --- | --- |
| 1 | Access Control | Installation, Programming, Customization, Commissioning of all items Access control items supplied (excluding spare) and its Trial run, Report formatting, Customization of report as per buyers requirement | lot | 1 |
| 2 | CCTV Surveillance system | Installation, Programming, Customization, Commissioning of all CCTV surveillance item supplied and its trial run. | Lot | 1 |

Acceptable Make:

| Access Control | Card Reader | Bosch, Honeywell, ESSL, godrej |
| --- | --- | --- |
|  | E/M Locks | ESSL, ADI, Honeywell, godrej, Star link, Shri Technology, Siddartha shutter |
| CCTV | Camera, DVR/NVR, Power supply, | Alcon, Hikvision, ACTi, Panasonic, Honeywell, |
| IT Equipments | Media converter, PoE Network switch, CCTV Monitor | Dlink, Digilink, Alcon, Cpplus, Hikvision |
| Display station | Monitor | LG, Samsung |
| Hardware equipment |  | Any reputed make |

Deviation Sheet: (Add more sheet if required)

| SL. No. | Page No. | Paragraph No. | Terms as per Tender | Deviation |
| --- | --- | --- | --- | --- |
| 1 |  |  |  |  |
| 2 |  |  |  |  |
| 3 |  |  |  |  |
| 4 |  |  |  |  |
| 5 |  |  |  |  |
| 6 |  |  |  |  |
| 7 |  |  |  |  |
| 8 |  |  |  |  |
| 9 |  |  |  |  |
| 10 |  |  |  |  |

Note: Add more pages if neccessary

(Signature of Bidder)

Stamp of the Firm

Price Schedule:

| SUPPLY PART |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | Sl. No. | Description of items | Unit | Quantity Required | Unit Price with GST | Total Amount |  |
| Access Control | 1 | Biometric Cum RFID Card reader | No. | 12 |  |  |  |
|  | 2 | Battery for Biometric cum RFID reader | No. | 12 |  |  |  |
|  | 3 | EM LOCKS | No. | 12 |  |  |  |
|  | 4 | EXIT BUTTON | No. | 12 |  |  |  |
|  | 5 | Misc. Hardware | lot | 1 |  |  |  |
| Subtotal of Supply for Access Control |  |  |  |  |  |  |  |  |
| Surveillance System | 6 | CCTV Camera (IP/Network) | No. | 8 |  |  |  |
|  | 7 | CCTV Camera (Analog) | No. | 4 |  |  |  |
|  | 8 | Power Supply for CCTV Camera | No. | 7 |  |  |  |
|  | 9 | 3+1 cable for Analog camera | Meter | 180 |  |  |  |
|  | 10 | DVR (4 - Channel) | No. | 4 |  |  |  |
|  | 11 | 1TB HDD for DVR/NVR | No. | 7 |  |  |  |
|  | 12 | 18.5" CCTV monitor | No. | 7 |  |  |  |
|  | 13 | UTP cable for IP Camera | Meter | 305 |  |  |  |
|  | 14 | NVR (8-Channel) | No. | 3 |  |  |  |
|  | 15 | Media Converter 10/100X | No. | 7 |  |  |  |
|  | 16 | PoE Network Switch | No. | 5 |  |  |  |
|  | 17 | Spare Mifare RFID Card | No. | 100 |  |  |  |
|  | 18 | Misc. Hardware (Junction box, Fiber optics patch cord sc type, Plug, Socket, wire, glands, lugs, cable tie, Cable etc.) | lot | 1 |  |  |  |
| Subtotal of Supply for Surveillance system |  |  |  |  |  |  |  |  |
| Total of Supply (Access Control & Surveillance system) |  |  |  |  |  |  |  |
| SERVICE PART |  |  |  |  |  |  |
| Access Control | 1 | Installation, Programming Commissioning of RFID cum Biometric reader, interface software, E/M locks, E/M locks, Trial run, report generation etc. | Lot | 1 |  |  |  |
| Subtotal of Services for Access Control |  |  |  |  |  |  |  |  |
| Surveillance System | 2 | Installation, Programming Commissioning of all items supplied & Trial run, etc. | Lot | 1 |  |  |  |
| Subtotal of Services for Surveillance system |  |  |  |  |  |  |  |  |
| Total of Service (Access Control & Surveillance system) |  |  |  |  |  |  |  |
| Total Estimated Cost (Supply and Service), incl. of GST |  |  |  |  |  |  |  |  |